## I_O List
TAG | TYPE | SCOPE | ADDRESS | MODULE | POINT | DESCRIPTION | FIELD DEVICE | BOM REF | WIRE # | TERMINAL | NOTES
I12 | DI | Permanent | _IO_EM_DI_12 | Embedded | I-12 | Load PSU fault input | AB 1606-CLP70 DC-OK signal contact | L3 - 24V PSU (load) [ADD TO BOM] |  |  | Monitors load PSU healthy signal. PLC logs fault if DC-OK drops.
I13 | DI | Permanent | _IO_EM_DI_13 | Embedded | I-13 | Red pushbutton (operator) | 22mm AB momentary PB - red | L7 - Push Buttons |  |  | Standard 22mm AB plastic PB
I14 | DI | Permanent | _IO_EM_DI_14 | Embedded | I-14 | Green pushbutton (operator) | 22mm AB momentary PB - green | L7 - Push Buttons |  |  | Standard 22mm AB plastic PB
I15 | DI | Permanent | _IO_EM_DI_15 | Embedded | I-15 | Blue pushbutton (operator) | 22mm AB momentary PB - blue | L7 - Push Buttons |  |  | Standard 22mm AB plastic PB
O0 | DO | Permanent | _IO_EM_DO_00 | Embedded | O-00 | Red indicator LED | 22mm AB 24VDC LED - red | L7 - LED Indicators |  |  | Direct-driven from PLC unless isolation needed
O1 | DO | Permanent | _IO_EM_DO_01 | Embedded | O-01 | Green indicator LED | 22mm AB 24VDC LED - green | L7 - LED Indicators |  |  | Direct-driven from PLC unless isolation needed
O2 | DO | Permanent | _IO_EM_DO_02 | Embedded | O-02 | Blue indicator LED | 22mm AB 24VDC LED - blue | L7 - LED Indicators |  |  | Direct-driven from PLC unless isolation needed

## Reserve_Planning
MODULE | POINT | ADDRESS | STATUS | ALLOCATION
Embedded | I-00 | _IO_EM_DI_00 | Reserved-Demo | Held for field demo cell input
Embedded | I-01 | _IO_EM_DI_01 | Reserved-Demo | Held for field demo cell input
Embedded | I-02 | _IO_EM_DI_02 | Reserved-Demo | Held for field demo cell input
Embedded | I-03 | _IO_EM_DI_03 | Reserved-Demo | Held for field demo cell input
Embedded | I-04 | _IO_EM_DI_04 | Reserved-Demo | Held for field demo cell input
Embedded | I-05 | _IO_EM_DI_05 | Reserved-Demo | Held for field demo cell input
Embedded | I-06 | _IO_EM_DI_06 | Reserved-Demo | Held for field demo cell input
Embedded | I-07 | _IO_EM_DI_07 | Reserved-Demo | Held for field demo cell input
Embedded | I-08 | _IO_EM_DI_08 | Reserved-Demo | Held for field demo cell input
Embedded | I-09 | _IO_EM_DI_09 | Reserved-Demo | Held for field demo cell input
Embedded | I-10 | _IO_EM_DI_10 | Reserved-Demo | Held for field demo cell input
Embedded | I-11 | _IO_EM_DI_11 | Reserved-Demo | Held for field demo cell input
Embedded | I-12 | _IO_EM_DI_12 | PERMANENT | see I_O List
Embedded | I-13 | _IO_EM_DI_13 | PERMANENT | see I_O List
Embedded | I-14 | _IO_EM_DI_14 | PERMANENT | see I_O List
Embedded | I-15 | _IO_EM_DI_15 | PERMANENT | see I_O List
Embedded | I-16 | _IO_EM_DI_16 | Reserved-Demo | Held for field demo cell input
Embedded | I-17 | _IO_EM_DI_17 | Reserved-Demo | Held for field demo cell input
Embedded | I-18 | _IO_EM_DI_18 | Reserved-Demo | Held for field demo cell input
Embedded | I-19 | _IO_EM_DI_19 | Reserved-Demo | Held for field demo cell input
Embedded | I-20 | _IO_EM_DI_20 | Reserved-Demo | Held for field demo cell input
Embedded | I-21 | _IO_EM_DI_21 | Reserved-Demo | Held for field demo cell input
Embedded | I-22 | _IO_EM_DI_22 | Reserved-Demo | Held for field demo cell input
Embedded | I-23 | _IO_EM_DI_23 | Reserved-Demo | Held for field demo cell input
Embedded | I-24 | _IO_EM_DI_24 | Reserved-Demo | Held for field demo cell input
Embedded | I-25 | _IO_EM_DI_25 | Reserved-Demo | Held for field demo cell input
Embedded | I-26 | _IO_EM_DI_26 | Reserved-Demo | Held for field demo cell input
Embedded | I-27 | _IO_EM_DI_27 | Reserved-Demo | Held for field demo cell input
Embedded | O-00 | _IO_EM_DO_00 | PERMANENT | see I_O List
Embedded | O-01 | _IO_EM_DO_01 | PERMANENT | see I_O List
Embedded | O-02 | _IO_EM_DO_02 | PERMANENT | see I_O List
Embedded | O-03 | _IO_EM_DO_03 | Reserved-Demo | Held for field demo cell output
Embedded | O-04 | _IO_EM_DO_04 | Reserved-Demo | Held for field demo cell output
Embedded | O-05 | _IO_EM_DO_05 | Reserved-Demo | Held for field demo cell output
Embedded | O-06 | _IO_EM_DO_06 | Reserved-Demo | Held for field demo cell output
Embedded | O-07 | _IO_EM_DO_07 | Reserved-Demo | Held for field demo cell output
Embedded | O-08 | _IO_EM_DO_08 | Reserved-Demo | Held for field demo cell output
Embedded | O-09 | _IO_EM_DO_09 | Reserved-Demo | Held for field demo cell output
Embedded | O-10 | _IO_EM_DO_10 | Reserved-Demo | Held for field demo cell output
Embedded | O-11 | _IO_EM_DO_11 | Reserved-Demo | Held for field demo cell output
Embedded | O-12 | _IO_EM_DO_12 | Reserved-Demo | Held for field demo cell output
Embedded | O-13 | _IO_EM_DO_13 | Reserved-Demo | Held for field demo cell output
Embedded | O-14 | _IO_EM_DO_14 | Reserved-Demo | Held for field demo cell output
Embedded | O-15 | _IO_EM_DO_15 | Reserved-Demo | Held for field demo cell output
Embedded | O-16 | _IO_EM_DO_16 | Reserved-Demo | Held for field demo cell output
Embedded | O-17 | _IO_EM_DO_17 | Reserved-Demo | Held for field demo cell output
Embedded | O-18 | _IO_EM_DO_18 | Reserved-Demo | Held for field demo cell output
Embedded | O-19 | _IO_EM_DO_19 | Reserved-Demo | Held for field demo cell output

## Hardwired_Logic
TAG | DEVICE | FUNCTION | POWER SOURCE | BOM REF | NOTES
KM-LOAD | WAGO 857-304 (24 VDC SPDT relay) | Load-enable contactor: E-stop NC in series with coil. Contact gates load PSU input. Drops out on E-stop press, removing power to load PSU. | 24 V control rail (NVVV HDR-100-24) | L4 - Relay Module (WAGO 857-304) | Hardwired safety path. PLC does NOT command this. Consider adding a DI to monitor coil/aux state for diagnostics in v0.2.
HL-LOAD | Pilot lamp across load PSU output | Visual indicator that load PSU output is live. Lit whenever load PSU is energized. | Load PSU output (AB 1606-CLP70, 24 VDC) | L7 - Pilot lamp [ADD TO BOM] | Hardwired across load PSU + and -. Not a PLC point. Confirms load power independent of PLC state - useful during E-stop / commissioning checks.
ESTOP-1 | 22 mm E-stop NC twist-release | Master E-stop. NC contact in series with KM-LOAD coil. | 24 V control rail | L4 - E-Stop | Single E-stop in v0.1. Add a PLC DI for E-stop status monitoring in v0.2 if program needs to react (vs just lose power).

## ACADE_Notes
PROJECT | MCC01 Control Panel - I/O List v0.1
PLC | Allen-Bradley Micro850, 2080-LC50-48QBB (28 DI / 20 DO embedded)
PROGRAMMING SW | Connected Components Workbench (CCW) - NOT RSLogix
ADDRESS FORMAT | _IO_EM_DI_xx for embedded inputs, _IO_EM_DO_xx for embedded outputs
POWER ARCHITECTURE
Control PSU | NVVV HDR-100-24 (24 VDC, 92 W) - powers PLC, relays, indicators, control logic
Load PSU | AB 1606-CLP70 (24 VDC, 70 W) - powers load circuits via WAGO 857-304 contact gated by E-stop
Safety PSU | WAGO 787-1200 (per BOM) - role TBD
SCOPE OF I_O List sheet | Permanent panel PLC I/O only. Spare embedded points + open terminal blocks are reserved for field-demo cell wiring. See Reserve_Planning sheet for full point map and Hardwired_Logic sheet for non-PLC devices.
AutoCAD Electrical workflow:
Option A - Manual (best for <10 PLC points) | Schematic > Insert Components > PLC (Parametric) for the module shell, then drop individual I/O point symbols on rungs. Type TAG/ADDRESS/DESC by hand from this sheet.
Option B - PLC I/O Utility (spreadsheet to drawing) | Schematic > Insert Components > PLC I/O Utility > Spreadsheet (.xls). ACADE columns: DESC1..DESC5, ADDRESS, RUNG, TAG, WIRE NUMBER, TERMINAL. Map: DESCRIPTION->DESC1, FIELD DEVICE->DESC2, NOTES->DESC3. ADDRESS, TAG, WIRE NUMBER, TERMINAL map directly.
Option C - From-scratch parametric | ACADE does not ship a Micro850 parametric. Skip for v0.1.
OPEN ITEMS
BOM update | Add AB 1606-CLP70 (load PSU) and load-side pilot lamp. Confirm control PSU brand.
E-stop monitoring | Currently hardwired only. Decide if a PLC DI should monitor E-stop state.
Wire numbering | Pick convention (1001+ vs signal-based) before populating WIRE #.